## Slide 1: Cyclic Spectral Analysis of Power Line Noise in the 3-200 kHz Band
Karl Nieman†, Jing Lin†, Marcel Nassar†, Khurram Waheed‡, Brian L. Evans†
†Department of Electrical and Computer Engineering, The University of Texas, Austin, TX USA
‡Freescale Semiconductor, Inc., Austin, TX USA
March 27, 2013

## Slide 2: Outline
Background
  Cyclostationary noise in PLC
  Cyclic spectral analysis
  Measurement setup
Measurement Campaigns
  Characterization of “cyclostationarity” of noise
Cyclic Bit Loading for G3-PLC
  Demonstrate 2x throughput increase
Background | Measurement Campaigns | Cyclic Bit Loading | Conclusion

## Slide 3: Cyclostationary Noise in Outdoor PLC
Both sites reveal time and frequency-periodic statistical properties
Example cyclic noise sources [Güzelgöz2010]
  motors, fluorescent bulbs, light dimmers, rectifying circuits, etc.
Medium Voltage Site
Low Voltage Site
Data collected jointly with Aclara and Texas Instruments near St. Louis, MO, USA.
fundamental period ≈ ½ AC cycle
lines separate statistically-similar regions
Background | Measurement Campaigns | Cyclic Bit Loading | Conclusion

## Slide 4: Cyclic Spectral Analysis [Gardner1986, Antoni2007]
Instantaneous auto-correlation function
is periodic w/ period if:
If periodic, accepts a Fourier transform
and coherence over frequency and cycle frequency can be defined as
cycle frequencies
“cyclic spectral coherence”
Background | Measurement Campaigns | Cyclic Bit Loading | Conclusion

## Slide 5: Example: 120 Hz AM White Noise
repeating statistical properties every half cycle = 240 Hz
Background | Measurement Campaigns | Cyclic Bit Loading | Conclusion

## Slide 6: Example: 120 Hz AM White Noise
decomposes into “stripe” at = 240 Hz
Background | Measurement Campaigns | Cyclic Bit Loading | Conclusion

## Slide 7: Measurement Setup
Used to collect noise samples at low-voltage sites
System configuration (G3-PLC CENELEC-A, 3-95 kHz):
Note: frames can span many AC cycles!
Background | Measurement Campaigns | Cyclic Bit Loading | Conclusion

## Slide 8: Measurement Sites in Austin, TX USA
San Jacinto
Office Engineering Sciences Building room 414
Industrial Hal C. Weever Power Plant Expansion
E 24th St
Residential Apartment complex ~2 mi North
Background | Measurement Campaigns | Cyclic Bit Loading | Conclusion

## Slide 9: Measurement Site 1: Office
weak narrowband f = 140 kHz
broadband impulse DC-30 kHz
strong narrowband f = 60, 65 kHz
Background | Measurement Campaigns | Cyclic Bit Loading | Conclusion

## Slide 10: Case Study 1: Office
highly sinusoidal at 120 Hz
Higher power, but less coherent at f = 60,65 kHz
impulse train is eigenfunction of FFT (spacing 120 Hz)
Background | Measurement Campaigns | Cyclic Bit Loading | Conclusion

## Slide 11: Measurement Site 2: Industrial
narrow impulses f = 10 kHz
broadband impulses f = 30-120 kHz
Background | Measurement Campaigns | Cyclic Bit Loading | Conclusion

## Slide 12: Measurement Site 2: Industrial
highly stationary 360 Hz impulses
less stationary 120 Hz structures
Background | Measurement Campaigns | Cyclic Bit Loading | Conclusion

## Slide 13: Measurement Site 3: Residential
complex spectrum f = 30-120 kHz
narrowband f = 140 kHz
frequency sweep f = 170 kHz
Background | Measurement Campaigns | Cyclic Bit Loading | Conclusion

## Slide 14: Measurement Site 3: Residential
though spectrally complex, many components have strong stationarity at 120 Hz
Background | Measurement Campaigns | Cyclic Bit Loading | Conclusion

## Slide 15: Cyclic Bit Loading for G3-PLC
RX measures SNR-per-subcarrier over ½ AC cycle
Exploit highly-colored yet cyclic noise to increase system throughput
12 G3-PLC symbols ≈ 8.34 ms
“Enhanced” tone map request is used to give TX 2-D bit allocation map
Background | Measurement Campaigns | Cyclic Bit Loading | Conclusion

## Slide 16: Link Throughput for Target BER = 10-2
Throughput increased by 2x in measured noise data
Further gains possible using larger modulation/rate codebook
2x increase!
Background | Measurement Campaigns | Cyclic Bit Loading | Conclusion

## Slide 17: Conclusions
Demonstrated utility of cyclic spectral analysis for PLC
Confirmed cyclostationarity of meaured noise components
Achieved 2x throughput increase using cyclic bit loading
Data and Matlab tools are available for download here:
http://users.ece.utexas.edu/~bevans/papers/2013/PLCcyclic/index.html
Background | Measurement Campaigns | Cyclic Bit Loading | Conclusion

## Slide 18: References
  M. Nassar, J. Lin, Y. Mortazavi, A. Dabak, I. H. Kim, and B. L. Evans, “Local Utility Powerline Communications in the 3-500 kHz Band: Channel Impairments, Noise, and Standards”, IEEE Signal Processing Magazine, Special Issue on Signal Processing Techniques for Smart Grid, Sep. 2012.
  S. Güzelgöz, H. B. Celebi, T. Guzel, H. Arslan, M. C. Mihcak, “Time Frequency Analysis of Noise Generated by Loads in PLC”, Proc. IEEE International Conference on Telecommunications, 2010.
  J. Antoni, “Cyclic Spectral Analysis in Practice,” Mechanical Systems and Signal Processing, 2007.
  M. Nassar, A. Dabak, I. H. Kim, T. Pande, and B. L. Evans, “Cyclostationary Noise Modeling in Narrowband Powerline Communication for Smart Grid Applications,” Proc. IEEE International Conference on Acoustics, Speech, and Signal Processing, 2012.
  W. Gardner, “The Spectral Correlation Theory of Cyclostationary Time-Series,” Signal Processing, 1986.
  S. Katar, B. Mashbum, K. Afkhamie, H. Latchman, and R. Newman, “Channel adaptation based on cyclo-stationary noise characteristics in PLC systems,” IEEE Intl. Symp. on Power Line Commun. and Its Appl.(ISPLC), pp. 16–21, 2006.
Background | Measurement Campaigns | Cyclic Bit Loading | Conclusion

## Slide 19: Noise Playback Testbed
G3 link using two Freescale PLC G3-OFDM modems
Software tools provided by Freescale allow frame-by-fame analysis
Test setup allows synchronous noise injection into power line
Freescale PLC G3-OFDM Modem
ESPL Freescale PLC Testbed in ENS 607
One modem was used to sample power line noise data in field
Collected 16k 16-bit 400 kS/s samples at each location
Backup